## Water Balance
Key: |  | Variables | Description | Units | Arrowtown (Excl. Millbrook) | Arthurs Point | Glenorchy | Hawea | Lake Hayes & Shotover Country | Lake Hayes | Shotover Country | Luggate | Queenstown | Wanaka | Wanaka Airport | Corbridge | QLDC Total
Excludes Millbrook
Water Supplied
Input cell | System Input | Period of Analysis | For period relating to latest SCADA flows | dd/mm/yy | 01/07/23 to 30/06/24 | 01/07/23 to 30/06/24 | 01/07/23 to 30/06/24 | 01/07/23 to 30/06/24 | 01/07/23 to 30/06/24 | 01/07/23 to 30/06/24 | 01/07/23 to 30/06/24 | 01/07/23 to 30/06/24 | 01/07/23 to 30/06/24 | 01/07/23 to 30/06/24 | 01/07/23 to 30/06/24 | 01/07/23 to 30/06/24 | 01/07/23 to 30/06/24
Calculation |  | Period |  | No. of Days | 366 | 366 | 366 | 366 | 366 | 366 | 366 | 366 | 366 | 366 | 366 | 366 | 366
Output |  | Volume Supplied | Sourced from SCADA (Daily flows) | m³ for Period | 1168959 | 331233 | 153844 | 751361 | 1200757.4 |  |  | 127650 | 5316768 | 4290682 | 26013 | 79360 | 13446627.4
Unreliable results |  | Water Exported | Billed water exported to other schemes/systems. Assume 10% growth since 2021 until actual flows known. | m³ for Period | 194856.5493
|  | Water Imported |  | m³ for Period
|  | Net Into Scheme / System | 2023/24 | m³ for Period | 974102.4507 | 331233 | 153844 | 751361 | 1200757.4 | 0 | 0 | 127650 | 5316768 | 4290682 | 26013 | 79360 | 13251770.8507
|  | 2020/21 figures | 2020/21 | m³ for Period | 828051.231 | 190844 | 205962.1613 | 478773.3252 | 1017002.3545 |  |  | 94160 | 4843075 | 3519466.9
|  | % change |  |  | 14.99% | 42.38% | -33.88% | 36.28% | 15.3% |  |  | 26.24% | 8.909% | 17.97%
| Key Inputs | Financial Data
|  | Volumetric Charge (excl. GST) |  | cents per m³
|  | Annual Cost of Running Water Supply System | 2021 LTP | $ per Year
|  | Cost of Production (Electricity and Chemicals) (excl. GST) | Estimate | cents per m³
Demand Assumptions (Un-Metered)
|  | Residential | Typical daily demand | litres per day per SUIP | 1000 | 750 | 550 | 900 | 700 | 900 | 700 | 900 | 900 | 1000 | 1000 | 1000
|  | Residential plus flat | Typical daily demand | litres per day per SUIP | 600 | 750 | 550 | 900 | 700 | 900 | 700 | 900 | 600 | 600 | 600 | 600
|  | Rural | Typical daily demand | litres per day per SUIP | 2000 | 2000 | 1200 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
|  | Accommodation | Typical daily demand | litres per day per SUIP | 700 | 700 | 525 | 350 | 350 | 350 | 700 | 700 | 700 | 700 | 700 | 700
|  | Commercial | Typical daily demand | litres per day per SUIP | 2000 | 2000 | 1050 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 2000 | 2000 | 2000
|  | Council facilities | Typical daily demand | litres per day per SUIP
|  | Parks Irrigation | Typical daily demand | litres per day per SUIP
Demand Assumptions (Metered)
|  | Residential | Typical daily demand | litres per day per connection |  |  | 550 |  |  |  |  | 900
|  | Residential plus flat | Typical daily demand | litres per day per connection |  |  | 550 |  |  |  |  | 900
|  | Rural | Typical daily demand | litres per day per connection
|  | Accommodation | Typical daily demand | litres per day per connection
|  | Commercial | Typical daily demand | litres per day per connection
|  | Council facilities | Typical daily demand | litres per day per connection
|  | Parks Irrigation | Typical daily demand | litres per day per connection
Demand Units
|  | Residential | Units of demand from rates database | Demand Units | 1353 | 422 | 193 | 1010 | 1967 | 1967 | 0 | 173 | 6805 | 6140
|  | Residential plus flat |  | Demand Units | 5 | 0 | 2 | 1 | 2 | 2 | 0 | 0 | 19 | 13
|  | Rural |  | Demand Units | 92 | 3 |  | 27 | 403 | 403 |  | 77 | 53 | 372 |  | 56
|  | Accommodation | Difference beteween SUIPS and Demand Units is win Accomodation land use | Demand Units | 158 | 92 | 86 | 139 | 172 | 172 |  | 2 | 4193 | 1464
|  | Commercial |  | Demand Units | 135 | 10 | 11 | 11 | 26 | 26 |  | 7 | 1375 | 589 | 30
|  | Council facilities |  | Demand Units
|  | Parks Irrigation |  | Demand Units
|  | Bulk Supply |  | Demand Units
Connections
|  | Residential | Used to calculate UARL only. | Connections | 5 |  | 1 | 1 | 2 | 2 |  |  | 12 | 13
|  | Residential plus flat | Used to calculate UARL only. | Connections | 1204 | 327 | 179 | 962 | 1627 | 1627 |  | 169 | 4006 | 5556
|  | Rural | Used to calculate UARL only. | Connections | 16 | 3 |  | 25 | 269 | 269 |  | 73 | 45 | 183
|  | Accommodation | Used to calculate UARL only. | Connections | 127 | 49 | 26 | 40 | 131 | 131 |  | 2 | 1009 | 787
|  | Commercial | Used to calculate UARL only. | Connections | 61 | 6 | 10 | 9 | 21 | 21 |  | 5 | 506 | 273
|  | Council facilities | Used to calculate UARL only. | Connections
|  | Parks Irrigation | Used to calculate UARL only. | Connections
|  | Bulk Supply | Used to calculate UARL only. | Connections | 1
Annual Demand
|  | Residential | Daily demand x connections, annualised | m³ for Period | 493845 | 115522.5 | 38744.75 | 331785 | 646159.5 | 646159.5 | 0 | 56830.5 | 2235442.5 | 2241100 | 0 | 0 | 6805589.25
|  | Residential plus flat |  | m³ for Period | 1095 | 0 | 401.5 | 328.5 | 657 | 657 | 0 | 0 | 4161 | 2847 | 0 | 0 | 10147
|  | Rural |  | m³ for Period | 67160 | 2190 | 0 | 19710 | 294190 | 294190 | 0 | 56210 | 38690 | 271560 | 0 | 40880 | 1084780
|  | Accommodation |  | m³ for Period | 40369 | 23506 | 16479.75 | 17757.25 | 21973 | 21973 | 0 | 511 | 1071311.5 | 374052 | 0 | 0 | 1587932.5
|  | Commercial |  | m³ for Period | 98550 | 7300 | 4215.75 | 5621 | 13286 | 13286 | 0 | 3577 | 702625 | 429970 | 21900 | 0 | 1300330.75
|  | Council facilities |  | m³ for Period | 4745 | 0 | 3102.5 | 1825 | 730 | 547.5 | 182.5 | 182.5 | 10767.5 | 3285 | 0 | 0 | 25367.5
|  | Parks Irrigation |  | m³ for Period | 6516 | 648 | 972 | 3240 | 3240 | 972 | 2268 | 324 | 21528 | 19872 | 0 | 0 | 59580
|  | Other | [14 empty] | 0
0
[5 empty] | 712280 | 149166.5 | 63916.25 | 380266.75 | 980235.5 | 977785 | 2450.5 | 117635 | 4084525.5 | 3342686 | 21900 | 40880 | 10873727
|  | No. of Un-Metered Residential Connections | Counted from rates database. Uses SUIPs as better reflects demand. | Demand Units | 1358 | 422 | 195 | 1011 | 1969 | 1969 | 0 | 173 | 6824 | 6153 | 0 | 0 | 20074
|  | No. of Un-Metered Non-Residential Connections | Counted from Water Meter Data by land use | Demand Units | 385 | 105 | 97 | 177 | 601 | 601 | 0 | 86 | 5621 | 2425 | 30 | 56 | 10184
|  | No. of Bulk Customer Connections |  | No. | 1 | [11 empty] | 1
|  | No. of Metered Residential Connections |  | No. | [12 empty] | 0
|  | No. of Metered Non-Residential Connections |  | No. | [12 empty] | 0
|  | Total No. of Connections |  | Demand Units | 1743 | 527 | 292 | 1188 | 2570 | 2570 | 0 | 259 | 12445 | 8578 | 30 | 56 | 30258
|  | Length of Mains |  | km | 40.7618 | 10.3964 | 12.4005 | 34.415 | 84.191 | 61.4594 | 22.7316 | 9.237 | 204.601 | 258.138 | 50 | 50 | 838.3318
|  | Density of Connections |  | conns/km | 42.7606 | 50.6905 | 23.5474 | 34.5198 | 30.5258 | 41.8162 | 0 | 28.0394 | 60.8257 | 33.2303 | 0.6 | 1.12 | 36.0931
|  | Average Pressure | Data source: 2014 Thomas consultants report |  | 58 | 82 | 40 | 76 | 58 | 58 | 58 | 67 | 67 | 58 | 58 | 58 | 58
|  | Check Lm x 20 + Ns (>3000) | If red, then calculation of UARL unreliable. |  | 2558.236 | 734.9286 | 540.0106 | 1876.3 | 4253.82 | 3799.1886 | 454.6314 | 443.74 | 16537.02 | 13740.76 | 1030 | 1056 | 47024.6352
Change in 2 years
| Authorised Consumption | Billing Data
|  | Billed Metered Residential Consumption | Residential Consumption = ( Residential connections + Residenital with flats ) x Annual Demand for each | m³ for Period | [12 empty] | 0
|  | Billed Metered Non-Residential Consumption | Non-Residential Consumption = (Rural + Accom + Commercial Connections) x Annual Demand for each | m³ for Period | [12 empty] | 0
|  | Bulk Customer Connection | Any large individual users. | m³ for Period | [12 empty] | 0
|  | Metered Reserve Irrigation | Reserve Irrigation = (Total reserves and toilets on potable supply) x Annual Demand for each | m³ for Period | [12 empty] | 0
|  | Billed Un-Metered Residential Consumption (Estimated) | All residential use should go in here technically | m³ for Period | 494940 | 115522.5 | 39146.25 | 332113.5 | 646816.5 | 646816.5 | 0 | 56830.5 | 2239603.5 | 2243947 | 0 | 0 | 6815736.25
|  | Billed Un-Metered Non-Residential Consumption (Estimated) | All non-residential use should go in here technically | m³ for Period | 206079 | 32996 | 20695.5 | 43088.25 | 329449 | 329449 | 0 | 60298 | 1812626.5 | 1075582 | 21900 | 40880 | 3973043.25
|  | Billed Un-Metered Reserve Irrigation (Estimated) |  | m³ for Period | [12 empty] | 0
|  |  | Check calcs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Billed Consumption |  | m³ for Period | 701019 | 148518.5 | 59841.75 | 375201.75 | 976265.5 | 976265.5 | 0 | 117128.5 | 4052230 | 3319529 | 21900 | 40880 | 10788779.5
|  | Residential Billed Consumption |  | litres/conn/day | 995.799 | 747.9508 | 548.4973 | 897.541 | 897.541 | 897.541 | 0 | 897.541 | 896.708 | 996.425 | 0 | 0
|  | Non-Residential Billed Consumption |  | litres/conn/day | 1462.4867 | 858.6001 | 582.939 | 665.1269 | 1497.7269 | 1497.7269 | 0 | 1915.6818 | 881.0766 | 1211.8551 | 1994.5355 | 1994.5355
|  | Consumption |  | litres/conn/day | 1098.8827 | 769.9967 | 559.9385 | 862.9136 | 1037.8957 | 1037.8957 | #DIV/0! | 1235.6109 | 889.6478 | 1057.327 | 1994.5355 | 1994.5355
Unbilled Authorised Consumption
|  | Estimated Unbilled, Un-Metered Irrigation Use | Estimated Unbilled, Un-Metered Irrigation Use | m³ for Period | 11261 | 648 | 4074.5 | 5065 | 3970 | 1519.5 | 2450.5 | 506.5 | 32295.5 | 23157 | 0 | 0 | 84947.5
|  | Authorised Unbilled Consumption (0.5% Water Supplied) | Authorised Unbilled Consumption (0.5% Water Supplied) | m³ for Period | 4870.5123 | 1656.165 | 769.22 | 3756.805 | 6003.787 | 0 | 0 | 638.25 | 26583.84 | 21453.41 | 130.065 | 396.8 | 66258.8543
|  | Unbilled Consumption | Unbilled Authorised Consumption |  | 16131.5123 | 2304.165 | 4843.72 | 8821.805 | 9973.787 | 1519.5 | 2450.5 | 1144.75 | 58879.34 | 44610.41 | 130.065 | 396.8 | 151206.3543
|  | Unbilled Authorised Consumption (Council Reserves and Toilets etc) |  | litres/conn/day | 25.287 | 11.946 | 45.3226 | 20.289 | 10.6034 | 1.6154 | 0 | 12.0762 | 12.9267 | 14.2092 | 11.8456 | 19.3599 | 13.6536
|  | Authorised Consumption |  | m³ for Period | 717150.5123 | 150822.665 | 64685.47 | 384023.555 | 986239.287 | 977785 | 2450.5 | 118273.25 | 4111109.34 | 3364139.41 | 22030.065 | 41276.8 | 10939985.8543
| Water Losses | Apparent Losses
non-physical losses of water within a water distribution system, typically associated with inaccuracies in metering and unauthorized consumption
|  | Unauthorised Consumption (0.1% of Water Supplied) | Unauthorised Consumption (0.1% of Water Supplied) | m³ for Period | 974.1025 | 331.233 | 153.844 | 751.361 | 1200.7574 | 0 | 0 | 127.65 | 5316.768 | 4290.682 | 26.013 | 79.36 | 13251.7709
|  | Customer Meter Under-registration (2.0% of Billed Consumption) | Customer Meter Under-registration (2.0% of Billed Consumption) | m³ for Period | 14020.38 | 2970.37 | 1196.835 | 7504.035 | 19525.31 | 19525.31 | 0 | 2342.57 | 81044.6 | 66390.58 | 438 | 817.6 | 215775.59
|  | Apparent Losses |  | m³ for Period | 14994.4825 | 3301.603 | 1350.679 | 8255.396 | 20726.0674 | 19525.31 | 0 | 2470.22 | 86361.368 | 70681.262 | 464.013 | 896.96 | 229027.3609
Real Losses
|  | Current Annual Real Losses (CARL) |  | m³ for Period | 241957.456 | 177108.732 | 87807.851 | 359082.049 | 193792.0456 | -997310.31 | -2450.5 | 6906.53 | 1119297.292 | 855861.328 | 3518.922 | 37186.24 | 2082757.6356
|  | The actual volume of water lost from the system due to leaks, breaks, and overflows |  | litres/sec | 7.6515 | 5.6007 | 2.7768 | 11.3553 | 6.1283 | -31.5381 | -0.077493 | 0.21841 | 35.3957 | 27.065 | 0.11128 | 1.1759 | 65.8634
|  |  |  | litres/conn/day | 379.2805 | 918.2232 | 821.617 | 825.8405 | 206.0259 | -1060.2691 | 0 | 72.8583 | 245.7364 | 272.6065 | 320.4847 | 1814.3169 | 188.0691
|  |  |  | m³/km_main/day | 16.2183 | 46.5452 | 19.3469 | 28.5079 | 6.2891 | -44.3364 | -0.29454 | 2.0429 | 14.9471 | 9.0588 | 0.19229 | 2.032 | 6.788
|  | Unavoidable Annual Real Losses (UARL) |  | m³/annum | 45052.1399 | 18219.4607 | 6669.4193 | 43548.1938 | 75607.3425 | 1834.3339 | 8662.0921 | 9133.111 | 333537.2942 | 243643.0743 | 19561.08 | 20001.416 | 831904.1888
|  | The UARL provides an estimate of the minimum level of real losses that can be expected in a well-managed water distribution system under current operating conditions. This helps utilities set realistic targets for leakage reduction and understand the potential for further improvement. | If red then calculation of UARL is unreliable due to small scheme size. | m³ for Period | 45175.5704 | 18269.377 | 6687.6917 | 43667.5039 | 75814.4859 | 1839.3595 | 8685.8238 | 9158.1333 | 334451.095 | 244310.5896 | 19614.672 | 20056.2144 | 834183.3784
|  |  |  | litres/sec | 1.4286 | 0.57774 | 0.21149 | 1.3809 | 2.3975 | 0.058166 | 0.27467 | 0.28961 | 10.5764 | 7.7259 | 0.62028 | 0.63424 | 26.3795
|  |  |  | litres/conn/day | 70.815 | 94.7179 | 62.5766 | 100.4294 | 80.6005 | 1.9555 | 0 | 96.6109 | 73.4271 | 77.8171 | 1786.4 | 978.5429 | 75.3252
|  |  |  | m³/km_main/day | 3.0281 | 4.8013 | 1.4735 | 3.4668 | 2.4604 | 0.081771 | 1.044 | 2.7089 | 4.4663 | 2.5859 | 1.0718 | 1.096 | 2.7187
|  | Water Losses |  | m³ for Period | 256951.9385 | 180410.335 | 89158.53 | 367337.445 | 214518.113 | -977785 | -2450.5 | 9376.75 | 1205658.66 | 926542.59 | 3982.935 | 38083.2 | 2311784.9965
| Key Metrics | Infrastructure Leakage Index (ILI) |  |  | 5.3559 | 9.6943 | 13.1298 | 8.2231 | 2.5561 | -542.2052 | 0 | 0.75414 | 3.3467 | 3.5032 | 0.1794 | 1.8541 | 2.4968
|  | Leakage Band |  |  | C | D | D | D | B | #N/A | A | A | B | B | A | A | B
|  | Non-Revenue Water |  | % Water Supplied | 28.03% | 55.16% | 61.1% | 50.06% | 18.7% | 0% | 0% | 8.242% | 23.78% | 22.63% | 15.81% | 48.49% | 19.77%
|  |  | Potential savings by fixing leaks | $ per Year | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
% Running Costs | bar: C to B
|  | Revenue Water (Total Cost less Non-Revenue Water) |  | $ per Year | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Billed Consumption |  | Billed
|  | Unbilled Consumption |  | Unbilled
|  | Apparent Losses |  | Apparent Losses
|  | Current Annual Real Losses (CARL) |  | Current Annual Real Losses (CARL)
|  | System Input |  | litres/conn/day | 1526.9547 | 1717.2831 | 1439.5164 | 1728.0294 | 1276.5595 | 0 | #DIV/0! | 1346.6042 | 1167.2711 | 1366.656 | 2369.1257 | 3871.975 | 1196.61
Share of Production
|  | Residential Billed Consumption |  | % | 50.81% | 34.88% | 25.45% | 44.2% | 53.87% | #DIV/0! | #DIV/0! | 44.52% | 42.12% | 52.3% | 0% | 0% | 51.43%
|  | Non-Residential Billed Consumption |  | % | 21.16% | 9.962% | 13.45% | 5.735% | 27.44% | #DIV/0! | #DIV/0! | 47.24% | 34.09% | 25.07% | 84.19% | 51.51% | 29.98%
|  | Authorised Unbilled Consumption |  | % | 1.656% | 0.6956% | 3.148% | 1.174% | 0.8306% | #DIV/0! | #DIV/0! | 0.8968% | 1.107% | 1.04% | 0.5% | 0.5% | 1.141%
|  | Water Losses |  | % | 26.38% | 54.47% | 57.95% | 48.89% | 17.87% | #DIV/0! | #DIV/0! | 7.346% | 22.68% | 21.59% | 15.31% | 47.99% | 17.45%
[5 empty] | 100% | 100% | 100% | 100% | 100% | #DIV/0! | #DIV/0! | 100% | 100% | 100% | 100% | 100% | 100%
Note on D98: Tom Lucas: Assumes no unbilled metered consumption.
Note on D115: Tom Lucas: Assumes system is pressurised 100% of the time.
Note on G128: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Need to extract Millbrook reveneue and expenditure, otherwise include.

## Council Use
Assumed Demand | m3/day | Comment
Small Toilet | 0.5 | 50 uses per day, 6 litres per flsu plus 2 litres per hand wash plus 100 litres for cleaning per day.
Toilet Block | 4 | As per above, but assume atleast 6 toilets and 1 urinal @ 1000 litres per day
Small Reserve | 0.88767 | Small irrigation systems assumed 30 L/minute X 60 minute X 180 days
Large Reserve | 9.863 | Large irrigation systems assumed 300L/min X 120 minute/day X 100 days
Source: Asset Data Dashboard
QLDC - PUBLIC TOILETS - WATER USE ASSESSMENT
| # of toilet blocks | # of small toilet facilities | Total # of toilet connections | Toilet Block @ 4m³/day | Small Facilities @ 0.5m³/day | Total toilet use
Supply Area | No. | No. | No. | m³ | m³ | m³
Queenstown | 6 | 11 | 17 | 8760 | 2007.5 | 10767.5
Wanaka | 1 | 10 | 11 | 1460 | 1825 | 3285
Arrowtown | 3 | 2 | 5 | 4380 | 365 | 4745
Lake Hayes Water | 0 | 3 | 3 | 0 | 547.5 | 547.5
Shotover Country | 0 | 1 | 1 | 0 | 182.5 | 182.5
Hawea | 1 | 2 | 3 | 1460 | 365 | 1825
Arthurs Point | 0 | 0 | 0 | 0 | 0 | 0
Glenorchy | 2 | 1 | 3 | 2920 | 182.5 | 3102.5
Luggate | 0 | 1 | 1 | 0 | 182.5 | 182.5
24637.5
QLDC - IRRIGATION SYSTEMS - WATER USE ASSESSMENT
Supply Area | # of small irrigation systems | # of large irrigation systems | Total # of Parks irrigation | Small Systems @ 324m³/annum | Large System @ 3,600m³/annum | TOTAL
| No. | No. | No. | m³ | m³ | m³
Queenstown | 22 | 4 | 26 | 7128 | 14400 | 21528
Wanaka | 28 | 3 | 31 | 9072 | 10800 | 19872
Arrowtown | 9 | 1 | 10 | 2916 | 3600 | 6516
Lake Hayes Water | 3 | 0 | 3 | 972 | 0 | 972
Shotover Country | 7 | 0 | 7 | 2268 | 0 | 2268
Hawea | 10 | 0 | 10 | 3240 | 0 | 3240
Arthurs Point | 2 | 0 | 2 | 648 | 0 | 648
Glenorchy | 3 | 0 | 3 | 972 | 0 | 972
Luggate | 1 | 0 | 1 | 324 | 0 | 324
|  |  |  | 27540 | 28800 | 56340
324
3600
2024 data
Toilets
Scheme Name | Number
ARROWTOWN | 5
GLENORCHY | 3
LAKE HAWEA | 3
LAKE HAYES | 3
LUGGATE | 2
QUEENSTOWN | 18
SHOTVR CTY | 1
WANAKA | 17
Irrigation Systems
Scheme Name | Number
ARROWTOWN | 10
ARTHURS PT | 2
GLENORCHY | 3
LAKE HAWEA | 10
LAKE HAYES | 3
LUGGATE | 1
QUEENSTOWN | 26
SHOTVR CTY | 7
WANAKA | 55

## Connections and SUIPs
From rates database
Scheme | Customer Category | Sub-Category | WaterConns | WaterSUIPs | WaterDemUnits | Difference (Absolute) |  |  | Values
Arrowtown | Commercial | Commercial | 1 | 1 | 1 | 0 | Scheme | Sub-Category2 | Connections | SUIPS | Demand Units
Arrowtown | Commercial | Commercial | 25 | 47 | 47 | 0 | Arrowtown | Residential | 5 | 5 | 5
Arrowtown | Commercial | Commercial Mixed use | 14 | 14 | 14 | 0 | Arrowtown | Residental plus flat | 1204 | 1353 | 1353
Arrowtown | Commercial | Commercial | 1 | 2 | 2 | 0 | Arrowtown | Rural | 16 | 92 | 92
Arrowtown | Accomodation | Accomodation Mixed use | 11 | 24 | 24 | 0 | Arrowtown | Accomodation | 127 | 152 | 158
Arrowtown | Vacant | Vacant | 46 | 46 | 46 | 0 | Arrowtown | Commerical | 61 | 135 | 135
Arrowtown | Residential | Residential | 5 | 5 | 5 | 0 | Arrowtown Total |  | 1413 | 1737 | 1743
Arrowtown | Rural | Rural | 2 | 2 | 2 | 0 | Arthur's Point | Residental plus flat | 327 | 422 | 422
Arrowtown | Accomodation | Accomodation Mixed use | 1 | 1 | 1 | 0 | Arthur's Point | Rural | 3 | 3 | 3
Arrowtown | Commercial | Commercial | 2 | 2 | 2 | 0 | Arthur's Point | Accomodation | 49 | 81 | 92
Arrowtown | Accomodation | Accomodation Mixed use | 2 | 4 | 4 | 0 | Arthur's Point | Commerical | 6 | 10 | 10
Arrowtown | Commercial | Commercial | 4 | 4 | 4 | 0 | Arthur's Point Total |  | 385 | 516 | 527
Arrowtown | Accomodation | Accomodation Mixed use | 1 | 1 | 1 | 0 | Glenorchy | Residential | 1 | 2 | 2
Arrowtown | Accomodation | Accomodation Mixed use | 92 | 92 | 92 | 0 | Glenorchy | Residental plus flat | 179 | 193 | 193
Arrowtown | Commercial | Commercial | 14 | 65 | 65 | 0 | Glenorchy | Accomodation | 26 | 28 | 86
Arrowtown | Rural | Rural Dwelling | 1 | 1 | 1 | 0 | Glenorchy | Commerical | 10 | 11 | 11
Arrowtown | Residential | Residental plus flat | 1166 | 1278 | 1278 | 0 | Glenorchy Total |  | 216 | 234 | 292
Arrowtown | Rural | Rural Dwelling | 13 | 89 | 89 | 0 | Hawea | Residential | 1 | 1 | 1
Arrowtown | Accomodation | Accomodation | 19 | 28 | 35 | 7 | Hawea | Residental plus flat | 962 | 1010 | 1010
Arrowtown | Accomodation | Accomodation | 1 | 2 | 1 | 1 | Hawea | Rural | 25 | 27 | 27
Arrowtown | Residential | Residental plus flat | 38 | 75 | 75 | 0 | Hawea | Accomodation | 40 | 43 | 139
Arthur's Point | Residential | Residental plus flat | 2 | 2 | 2 | 0 | Hawea | Commerical | 9 | 11 | 11
Arthur's Point | Rural | Rural | 1 | 1 | 1 | 0 | Hawea Total |  | 1037 | 1092 | 1188
Arthur's Point | Commercial | Commercial Mixed use | 1 | 1 | 1 | 0 | Lake Hayes | Residential | 2 | 2 | 2
Arthur's Point | Vacant | Vacant | 1 | 1 | 1 | 0 | Lake Hayes | Residental plus flat | 1627 | 1967 | 1967
Arthur's Point | Residential | Residental plus flat | 8 | 16 | 16 | 0 | Lake Hayes | Rural | 269 | 403 | 403
Arthur's Point | Residential | Residental plus flat | 1 | 2 | 2 | 0 | Lake Hayes | Accomodation | 131 | 184 | 172
Arthur's Point | Vacant | Vacant | 30 | 30 | 30 | 0 | Lake Hayes | Commerical | 21 | 26 | 26
Arthur's Point | Commercial | Commercial | 5 | 9 | 9 | 0 | Lake Hayes Total |  | 2050 | 2582 | 2570
Arthur's Point | Rural | Rural Dwelling | 2 | 2 | 2 | 0 | Luggate | Residental plus flat | 169 | 173 | 173
Arthur's Point | Accomodation | Accomodation Mixed use | 33 | 40 | 40 | 0 | Luggate | Rural | 73 | 77 | 77
Arthur's Point | Vacant | Vacant | 1 | 1 | 1 | 0 | Luggate | Accomodation | 2 | 2 | 2
Arthur's Point | Residential | Residental plus flat | 12 | 26 | 26 | 0 | Luggate | Commerical | 5 | 7 | 7
Arthur's Point | Accomodation | Accomodation | 16 | 41 | 52 | 11 | Luggate Total |  | 249 | 259 | 259
Arthur's Point | Residential | Residental plus flat | 304 | 376 | 376 | 0 | Queenstown | Residential | 12 | 19 | 19
Glenorchy | Accomodation | Accomodation | 9 | 10 | 68 | 58 | Queenstown | Residental plus flat | 4006 | 6805 | 6805
Glenorchy | Accomodation | Accomodation Mixed use | 16 | 16 | 16 | 0 | Queenstown | Rural | 45 | 53 | 53
Glenorchy | Commercial | Commercial | 10 | 11 | 11 | 0 | Queenstown | Accomodation | 1009 | 2684 | 4193
Glenorchy | Residential | Residental plus flat | 1 | 2 | 2 | 0 | Queenstown | Commerical | 506 | 1375 | 1375
Glenorchy | Accomodation | Accomodation Mixed use | 1 | 2 | 2 | 0 | Queenstown Total |  | 5578 | 10936 | 12445
Glenorchy | Vacant | Vacant | 121 | 121 | 121 | 0 | Wanaka | Residential | 13 | 13 | 13
Glenorchy | Residential | Residental plus flat | 174 | 183 | 183 | 0 | Wanaka | Residental plus flat | 5556 | 6140 | 6140
Glenorchy | Residential | Residental plus flat | 4 | 8 | 8 | 0 | Wanaka | Rural | 183 | 372 | 372
Glenorchy | Residential | Residential | 1 | 2 | 2 | 0 | Wanaka | Accomodation | 787 | 1187 | 1464
Hawea | Accomodation | Accomodation | 4 | 4 | 100 | 96 | Wanaka | Commerical | 273 | 589 | 589
Hawea | Rural | Rural Dwelling | 21 | 21 | 21 | 0 | Wanaka Total |  | 6812 | 8301 | 8578
Hawea | Accomodation | Accomodation Mixed use | 2 | 4 | 4 | 0 | Grand Total |  | 17740 | 25657 | 27602
Hawea | Accomodation | Accomodation Mixed use | 32 | 33 | 33 | 0
Hawea | Commercial | Commercial Mixed use | 5 | 5 | 5 | 0
Hawea | Residential | Residental plus flat | 927 | 945 | 945 | 0
Hawea | Residential | Residental plus flat | 30 | 60 | 60 | 0
Hawea | Residential | Residential | 1 | 1 | 1 | 0
Hawea | Hydro/Utility | Hydro/Utility | 1 | 1 | 1 | 0
Hawea | Commercial | Commercial | 1 | 1 | 1 | 0
Hawea | Rural | Rural | 3 | 4 | 4 | 0
Hawea | Commercial | Commercial | 3 | 5 | 5 | 0
Hawea | Accomodation | Accomodation Mixed use | 2 | 2 | 2 | 0
Hawea | Vacant | Vacant | 288 | 288 | 288 | 0
Hawea | Residential | Residental plus flat | 5 | 5 | 5 | 0
Hawea | Rural | Rural Dwelling plus Flat | 1 | 2 | 2 | 0
Lake Hayes | Commercial | Commercial - Mixed Use | 3 | 3 | 3 | 0
Lake Hayes | Accomodation | Accomodation Mixed use | 1 | 1 | 1 | 0
Lake Hayes | Rural | Rural Dwelling | 4 | 5 | 5 | 0
Lake Hayes | Rural | Rural | 12 | 14 | 14 | 0
Lake Hayes | Residential | Residental plus flat | 1 | 1 | 1 | 0
Lake Hayes | Residential | Residental plus flat | 1 | 2 | 2 | 0
Lake Hayes | Rural | Rural Dwelling plus Flat | 6 | 12 | 12 | 0
Lake Hayes | Accomodation | Accomodation Mixed use | 1 | 2 | 2 | 0
Lake Hayes | Vacant | Vacant | 3 | 3 | 3 | 0
Lake Hayes | Rural | Rural Dwelling | 1 | 1 | 1 | 0
Lake Hayes | Rural | Rural | 17 | 18 | 18 | 0
Lake Hayes | Commercial | Commercial | 6 | 7 | 7 | 0
Lake Hayes | Residential | Residental plus flat | 1 | 2 | 2 | 0
Lake Hayes | Commercial | Commercial | 3 | 6 | 6 | 0
Lake Hayes | Vacant | Vacant | 164 | 164 | 164 | 0
Lake Hayes | Residential | Residental plus flat | 1 | 1 | 1 | 0
Lake Hayes | Accomodation | Accomodation Mixed use | 37 | 74 | 74 | 0
Lake Hayes | Residential | Residential | 2 | 2 | 2 | 0
Lake Hayes | Accomodation | Accomodation | 12 | 13 | 1 | 12
Lake Hayes | Rural | Rural Dwelling | 229 | 353 | 353 | 0
Lake Hayes | Accomodation | Accomodation Mixed use | 29 | 38 | 38 | 0
Lake Hayes | Accomodation | Accomodation Mixed use | 47 | 48 | 48 | 0
Lake Hayes | Commercial | Commercial Mixed use | 9 | 10 | 10 | 0
Lake Hayes | Residential | Residental plus flat | 1314 | 1339 | 1339 | 0
Lake Hayes | Accomodation | Accomodation Mixed use | 4 | 8 | 8 | 0
Lake Hayes | Residential | Residental plus flat | 309 | 622 | 622 | 0
Luggate | Accomodation | Accomodation Mixed use | 1 | 1 | 1 | 0
Luggate | Residential | Residental plus flat | 166 | 167 | 167 | 0
Luggate | Vacant | Vacant | 45 | 45 | 45 | 0
Luggate | Rural | Rural Dwelling | 69 | 70 | 70 | 0
Luggate | Vacant | Vacant | 1 | 1 | 1 | 0
Luggate | Commercial | Commercial | 1 | 1 | 1 | 0
Luggate | Rural | Rural | 1 | 1 | 1 | 0
Luggate | Commercial | Commercial | 4 | 6 | 6 | 0
Luggate | Accomodation | Accomodation Mixed use | 1 | 1 | 1 | 0
Luggate | Rural | Rural Dwelling plus Flat | 3 | 6 | 6 | 0
Luggate | Residential | Residental plus flat | 3 | 6 | 6 | 0
Queenstown | Rural | Rural Dwelling plus Flat | 1 | 2 | 2 | 0
Queenstown | Accomodation | Accomodation Mixed use | 82 | 167 | 167 | 0
Queenstown | Accomodation | Accomodation Mixed use | 1 | 2 | 2 | 0
Queenstown | Residential | Residental plus flat | 698 | 1472 | 1472 | 0
Queenstown | Rural | Rural Dwelling plus Flat | 5 | 10 | 10 | 0
Queenstown | Vacant | Vacant | 1121 | 1127 | 1127 | 0
Queenstown | Vacant | Vacant | 2 | 2 | 2 | 0
Queenstown | Residential | Residental plus flat | 1 | 1 | 1 | 0
Queenstown | Commercial | Commercial - Mixed Use | 1 | 1 | 1 | 0
Queenstown | Accomodation | Accomodation Mixed use | 549 | 692 | 692 | 0
Queenstown | Residential | Residental plus flat | 1 | 1 | 1 | 0
Queenstown | Rural | Rural | 3 | 3 | 3 | 0
Queenstown | Residential | Residential | 11 | 18 | 18 | 0
Queenstown | Accomodation | Accomodation Mixed use | 2 | 2 | 2 | 0
Queenstown | Residential | Residental plus flat | 3300 | 5322 | 5322 | 0
Queenstown | Commercial | Commercial | 1 | 1 | 1 | 0
Queenstown | Commercial | Commercial | 3 | 3 | 3 | 0
Queenstown | Accomodation | Accomodation Mixed use | 1 | 2 | 2 | 0
Queenstown | Rural | Rural | 4 | 4 | 4 | 0
Queenstown | Commercial | Commercial | 1 | 1 | 1 | 0
Queenstown | Accomodation | Accomodation Mixed use | 1 | 1 | 1 | 0
Queenstown | Commercial | Commercial | 344 | 866 | 866 | 0
Queenstown | Commercial | Commercial | 3 | 4 | 4 | 0
Queenstown | Residential | Residental plus flat | 2 | 4 | 4 | 0
Queenstown | Residential | Residential | 1 | 1 | 1 | 0
Queenstown | Accomodation | Accomodation Mixed use | 1 | 1 | 1 | 0
Queenstown | Commercial | Commercial | 2 | 2 | 2 | 0
Queenstown | Rural | Rural Dwelling | 28 | 29 | 29 | 0
Queenstown | Commercial | Commercial Mixed use | 24 | 26 | 26 | 0
Queenstown | Commercial | Commercial | 12 | 12 | 12 | 0
Queenstown | Commercial | Commercial | 3 | 3 | 3 | 0
Queenstown | Residential | Residental plus flat | 1 | 2 | 2 | 0
Queenstown | Residential | Residental plus flat | 3 | 3 | 3 | 0
Queenstown | Commercial | Commercial | 110 | 452 | 452 | 0
Queenstown | Rural | Rural Dwelling | 4 | 5 | 5 | 0
Queenstown | Accomodation | Accomodation Mixed use | 3 | 3 | 3 | 0
Queenstown | Commercial | Commercial - Mixed Use | 2 | 4 | 4 | 0
Queenstown | Accomodation | Accomodation | 351 | 1756 | 2974 | 1218
Queenstown | Accomodation | Accomodation | 18 | 58 | 349 | 291
Wanaka | Accomodation | Accomodation | 1 | 1 | 0 | 1
Wanaka | Rural | Rural Dwelling | 3 | 3 | 3 | 0
Wanaka | Rural | Rural | 4 | 4 | 4 | 0
Wanaka | Commercial | Commercial | 2 | 2 | 2 | 0
Wanaka | Residential | Residental plus flat | 19 | 19 | 19 | 0
Wanaka | Accomodation | Accomodation Mixed use | 564 | 609 | 609 | 0
Wanaka | Rural | Rural | 1 | 1 | 1 | 0
Wanaka | Commercial | Commercial | 1 | 3 | 3 | 0
Wanaka | Accomodation | Accomodation Mixed use | 18 | 20 | 20 | 0
Wanaka | Accomodation | Accomodation Mixed use | 3 | 6 | 6 | 0
Wanaka | Accomodation | Accomodation Mixed use | 50 | 99 | 99 | 0
Wanaka | Residential | Residental plus flat | 1 | 2 | 2 | 0
Wanaka | Accomodation | Accomodation Mixed use | 2 | 2 | 2 | 0
Wanaka | Accomodation | Accomodation | 1 | 1 | 0 | 1
Wanaka | Residential | Residential | 9 | 9 | 9 | 0
Wanaka | Commercial | Commercial | 3 | 3 | 3 | 0
Wanaka | Accomodation | Accomodation Mixed use | 1 | 2 | 2 | 0
Wanaka | Rural | Rural | 21 | 21 | 21 | 0
Wanaka | Residential | Residental plus flat | 175 | 352 | 352 | 0
Wanaka | Rural | Rural Dwelling plus Flat | 14 | 26 | 26 | 0
Wanaka | Residential | Residential | 4 | 4 | 4 | 0
Wanaka | Vacant | Vacant | 1 | 1 | 1 | 0
Wanaka | Hydro/Utility | Hydro/Utility | 1 | 1 | 1 | 0
Wanaka | Commercial | Commercial | 58 | 182 | 182 | 0
Wanaka | Rural | Rural Dwelling | 138 | 313 | 313 | 0
Wanaka | Commercial | Commercial | 5 | 5 | 5 | 0
Wanaka | Rural | Rural Dwelling plus Flat | 1 | 2 | 2 | 0
Wanaka | Vacant | Vacant | 1186 | 1190 | 1190 | 0
Wanaka | Commercial | Commercial | 1 | 1 | 1 | 0
Wanaka | Residential | Residental plus flat | 3 | 3 | 3 | 0
Wanaka | Accomodation | Accomodation | 137 | 416 | 635 | 219
Wanaka | Commercial | Commercial Mixed use | 17 | 18 | 18 | 0
Wanaka | Accomodation | Accomodation Mixed use | 2 | 2 | 2 | 0
Wanaka | Residential | Residental plus flat | 5358 | 5764 | 5764 | 0
Wanaka | Commercial | Commercial | 5 | 5 | 5 | 0
Wanaka | Accomodation | Accomodation | 8 | 29 | 89 | 60
Wanaka | Commercial | Commercial | 181 | 370 | 370 | 0
Wanaka | Rural | Rural Dwelling plus Flat | 1 | 2 | 2 | 0
1975

## Pipes and Pressure
2021 Scheme Water Supply Pipe length (from 3 Waters AMP scheme summaries)
| Supply | Trunk | Service | Rider | Rising | NA | Risefall | Fall | 2021 Reticulation pipe length (km) | Average System Pressure (metres of head) | 2024 Retic Length | Diff to 2021
Arrowtown | 25447 | 1464 | 5945 | 5197 | 1047 | 19 |  | 1637 | 40.756 | 58 | 7.3274 | -33.4286
Arthurs Point | 8377 |  | 1328 | 1730 | 946 | 5 |  |  | 12.386 | 82 | 1.4338 | -10.9522
Glenorchy | 7914 |  | 944 | 668 | 1206 | 678 |  |  | 11.41 | 40 | 1.226 | -10.184
Lake Hawea | 18779 | 1063 | 7082 | 4848 | 181 | 2035 | 427 |  | 34.415 | 76 | 9.1083 | -25.3067
Lake Hayes combined | 48692 | 5293 | 6750 | 17400 | 5766 | 290 |  |  | 84.191 | 58
Lake Hayes | [8 empty] | 0 |  | 3.9188 | 3.9188
Shotover | [8 empty] | 0 |  | 2.7297 | 2.7297
Luggate | 6822 |  | 991 | 983 | 441 |  |  |  | 9.237 | 67 | 1.21 | -8.027
Queenstown | 117297 | 34449 | 25299 | 15845 | 6003 | 3337 | 2371 |  | 204.601 | 67 | 26.7498 | -177.8512
Wanaka | 161854 | 43092 | 32570 | 11188 | 5795 | 3462 | 177 |  | 258.138 | 58 | 39.0013 | -219.1367
[9 empty] | 655.134 | Data source: 2014 Thomas consultants report | 92.7051 | -478.2379
2024 From Asset Register
Total Length of Network
| Watersupply Mains (km) | Watersupply Laterals (km) | TOTAL
ARROWTOWN | 33.4344 | 7.3274 | 40.7618
ARTHURS POINT | 10.3964 | 1.4338 | 11.8303
GLENORCHY | 12.4005 | 1.226 | 13.6266
LAKE HAWEA | 35.485 | 9.1083 | 44.5932
LAKE HAYES | 38.3201 | 3.9188 | 42.2389
LUGGATE | 5.7402 | 1.21 | 6.9502
QUEENSTOWN | 152.3857 | 26.7498 | 179.1355
SHOTOVER | 5.6264 | 2.7297 | 8.356
WANAKA | 197.9168 | 39.0013 | 236.9182

## Demand Assumptions
Consumption Data Assumptions
The following demand is assumed for each land use type
| Non-Metered Water Use | Description | Units | Data Source | Arrowtown (excl Millbrook) | Arthurs Point | Glenorchy | Hawea | Lake Hayes | Luggate | Shotover Country | Queenstown | Wanaka | Wanaka Airport | Corbridge
[5 empty] | AT | AP | GY | HW | LH | LG | SC | QT | WK
| Residential | Typical daily demand | litres per day per connection |  | 1000 | 750 | 1200 | 900 | 700 | 900 | 700 | 900 | 1000 | 1000 | 1000
| Residential plus flat | Typical daily demand | litres per day per connection |  | 600 |  | 600 | 600 | 600 | 600 | 300 | 600 | 600 | 600 | 600
| Rural | Typical daily demand | litres per day per connection |  | 2000 | 2000 | 1200 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
| Accommodation | Typical daily demand | litres per day per connection |  | 700 | 700 | 525 | 350 | 350 | 350 | 700 | 700 | 700 | 700 | 700
| Commercial | Typical daily demand | litres per day per connection |  | 2000 | 2000 | 1050 | 1400 | 1400 | 1400 | 1400 | 1400 | 2000 | 2000 | 2000
| Council facilities | Typical daily demand
| Parks Irrigation | Typical daily demand
| Metered Water Use |  |  |  | Arrowtown (excl Millbrook) | Arthurs Point | Glenorchy | Hawea | Lake Hayes | Luggate | Shotover Country | Queenstown | Wanaka | Wanaka Airport | Corbridge
[5 empty] | AT | AP | GY | HW | LH | LG | SC | QT | WK
| Residential | Typical daily demand | litres per day per connection |  | GY: 550; LG: 900
| Residential plus flat | Typical daily demand | litres per day per connection |  | GY: 550; LG: 900
| Rural | Typical daily demand | litres per day per connection
| Accommodation | Typical daily demand | litres per day per connection
| Commercial | Typical daily demand | litres per day per connection
| Council facilities | Typical daily demand
| Parks Irrigation | Typical daily demand
[5 empty] | Arrowtown (excl Millbrook) | Arthurs Point | Glenorchy | Hawea | Lake Hayes | Luggate | Shotover Country | Queenstown | Wanaka | Wanaka Airport | Corbridge
| SUIPs |  |  | Data Source | AT | AP | GY | HW | LH | LG | SC | QT | WK
| Residential | Total demand units | SUIPS | Rates database 1 july 2024 | AT: 100 |  | 29
| Residential plus flat |  |  | Rates database 1 july 2024 | AT: 29
| Rural |  |  | Rates database 1 july 2024 | AT: 234
| Accommodation |  |  | Rates database 1 july 2024
| Commercial |  |  | Rates database 1 july 2024 | [9 empty] | 20
| Council facilities |  |  | Rates database 1 july 2024
| Parks Irrigation |  |  | Rates database 1 july 2024
Annual Demand
| Residential |  | m3 for the period |  | 42968.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10614
| Non-Residential |  | m3 for the period |  | 171288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14640 | 0
| Reserves and Toilets |  | m3 for the period |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Production from Bores / Intakes
| Scada | 1/07/23 to 30/06/24 | From Rebecca Macfarlane email 8th Jul 2024
Arrowtown | Arrowtown | 1168959
| Arthurs point | 331233
Corbridge | Corbridge | 79360
| Glenorchy | 153844
| Hawea | 751361
Lake Hayes | JonesAve/LakeHayes | 783779.8
Lake Hayes | WildingRd/Lakehayes | 416977.6
| Luggate | 127650
Queenstown | Kelvin Heights | 2150691
Queenstown | Two Mile | 3163813
Queenstown | SoC borefield(new) | 2264
Wanaka Airport | Wanaka Airport | 26013
Wanaka | Beacon Point | 3654417
Wanaka | Western | 636265
Arrowtown | Millbrook | 194856.5493 | Demand in crease assumed at 22%
Lake Hayes | Bendemeer Supply

## Leakage Estimate
Nightflow assessment by Veolia
Figures are in litres per second |  |  |  |  | Survey Year
Area | Scheme | Zone | 2024 | 2023 | 2022 | 2021 | 2020 | 2019 | 2018 | 2017 | 2016 | m3/ day | per year | Annual Production |  | % Losses (Night Flow) | % Losses (Water Balance)
Wakatipu | Arrowtown | Arrowtown Main Zone | 13.07 | 17.39 | 12.26 | 11 | 4.5 | 15.9 | 15.5 | 14.3 | 1.3
|  | Cotter Ave & Advance Terrace | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Millbrook | 0.9' | 3.4 | 3.2 | 3.1 | 3.9 | 0.09 | 2.05 | 4.1 | 0
|  | Retirement Village | 0.1' | 0.8 | 0 | 0 | 0
|  | Manse Rd | 3 | 3 | 2.8 | 1.5
| Arrowtown Total |  | 19.07 | 24.59 | 18.26 | 15.6 | 8.4 | 15.99 | 17.55 | 18.4 | 1.3 | 1647.648 | 601391.52 | 1168959 | Arrowtown | 51.45% | 26.38%
| Arthurs Point | Arthurs Point East | 3.1 | 3.1 | 3.2 | 0.9 | 0.7 | 3 | 1.5 | 0.8 | 0.3
|  | Arthurs Point West | 1.99 | 0.16 | 0.21 | 0.63 | 0.24 | 0.07 | 0.2 | 0.1 | 0.2
| Arthurs Point Total |  | 5.09 | 3.26 | 3.41 | 1.53 | 0.94 | 3.07 | 1.7 | 0.9 | 0.5 | 439.776 | 160518.24 | 331233 | Arthurs Point | 48.46% | 54.47%
| Glenorchy | Glenorchy | 1.8 | 1.9 | 0.8 | 5 | 3.1 | 0.8 | 1.1 | 2
| Glenorchy Total |  | 1.8 | 1.9 | 0.8 | 5 | 3.1 | 0.8 | 1.1 | 2 | 1 | 155.52 | 56764.8 | 153844 | Glenorchy | 36.9% | 57.95%
| Queenstown | Boydtown | 0.9 | 2.4 | 4 | 3.3 | 6.4 | 3.8 | 1.1 | 2.8 | 4
|  | Central Gorge Road | 2.11 | 0.67 | 0.57 | 1.1 | 0.09 | 0.6 | 0.89 | 0.6 | 1.2
|  | Upper Gorge Road | 1.09 | 1.51 | 0.41 | 0.49 | 0.21 | 0.4 | 1.2 | 0.8 | 0.7
|  | Commonage | 3.9 | 4.7 | 20 | 19.9 | 21.2 | 1 | 0.5 | 6.1 | 5.2
|  | Frankton Road | 1.2 | 6.5 | 6.7 | 5 | 10.5 | 10.1 | 10.1 | 4.8 | 12.3
|  | Hallenstein Street | 0.9 | 0 | 1 | 1.1 | 0 | 0 | 0.8 | 1.4 | 3.8
|  | Goldfield Heights | 0.1 | 1.6 | 1.2 | 2 | 1.3 | 0.1 | 0.8 | 0.5 | 0.5
|  | Larchwood | 1.8 | 1.7 | 1.6 | 1.6 | 1.6 | 0 | 0.5 | 0.9 | 2
|  | Manchester Place | 0.2 | 0.5 | 0.2 | 0.2 | 0.7 | 0 | 0 | 0.3 | 1.3
|  | Queenstown CBD | 10.4 | 13 | 8 | 7.3 | 15.1 | 9.7 | 13.7 | 22.3 | 74.4
| Queenstown Total |  | 22.6 | 32.58 | 43.68 | 41.99 | 57.1 | 37.1 | 38.39 | 68.3 | 140.1 | 1952.64 | 712713.6
| Frankton | Frankton | 11.96 | 5.9 | 6.7 | 11.2 | 8.2 |  |  | 9 | 7.9
|  | Kelvin Heights East | 1.3 | 0.8 | 2.3 | 2.5 | 1.9 | 0 | 0 | 0.9 | 0
|  | Kelvin Heights West | 1.7 | 2.4 | 0.2 | 0.2 | 0 | 2 | 3.7 | 2.7 | 5.2
|  | Hanleys Farm | 2.04 | 0 | 0.2 | 0 | 0.06
|  | Quail Rise | 21.2 | 1.1 | 0.3 | 0.3 | 0 | 0 | 0.6 | 5.4 | 1.2
|  | Middleton Rd |  | 0 | 0 | 0 | 0
|  | Marina Drive | 0.3 | 0 | 0.1 | 3.9 | 3.4
| Frankton Total |  | 38.5 | 10.2 | 9.8 | 18.1 | 13.56 |  |  |  |  | 3326.4 | 1214136
|  | Heritage Hotel | 2.3 | 2.2 | 1.8 | 1.9 | 0 |  | 0.7
|  | Sunshine Bay | 2 | 1.2 | 1.6 | 1.6 | 3.5 | 2.6 | 1.3 | 1.3 | 1.1
|  | Lower Fernhill | 6.4 | 5.4 | 5.5 | 1.8 | 0.4 | 1.8 | 1.8 | 0.5 | 5.2
|  | Mid Fernhill | 2.6 | 19.7 | 1.6 | 1.6 | 4.1 | 1.5 | 0.7 | 8
|  | Upper Fernhill | 1.2 | 1.8 | 1.8 | 2 | 3.6 | 3.5
| Fernhill Total |  | 14.5 | 30.3 | 12.3 | 8.9 | 11.6 | 9.4 | 4.5 | 9.8 | 12.7 | 1252.8 | 457272
Wakatipu Total |  |  | 101.56 | 105.13 | 88.25 | 91.12 | 94.7 | 56.96 | 58.74 | 89.6 | 142.9 | 8774.784 | 3202796.16 | 5316768 | Queenstown | 60.24% | 22.68%
Wanaka | Hawea | Hawea east | 7 | 0.8 | 0.2 | 4.3 |  | 0.4 | 0.79 | 0.7 | 0.6
|  | Hawea west | 2 | 1.9 | 1.7 | 1.7 |  | 0.2 | 2.49 | 1.2 | 0.3
| Hawea Total |  | 9 | 2.7 | 1.9 | 6 | 2.3 | 0.6 | 3.28 | 1.9 | 0.9 | 777.6 | 283824 | 751361 | Hawea | 37.77% | 48.89%
| Luggate Total | Luggate | 1.2 | 0.8 | 0.7 | 0.3 | 0.8 | 0.3 | 0.5 | 0.7 | 0.5 | 103.68 | 37843.2 | 127650 | Luggate | 29.65% | 7.346%
| Wanaka | Albert Town | 8.3 | 3.8 | 2.3 | 2.2 | 2.2 | 0 | 3.3 | 3.2 | 5
|  | Anderson Road & Mount Iron Estate | 5.3 | 2.1 | 2.1 | 2.1 | 2.1 | 0.1 | 0 | 0.1
|  | Ballantyne Road & Industrial Area | 8.3 | 0.9 | 0.3 | 0.5 | 0.2 | 0.5 | 0.19 | 0.2 | 0.3
|  | Hedditch Street | 0.3 | 0 | 0 | 0 | 2.2 | 2.4 | 1.4 | 2
|  | Peninsula Bay & Kings Drive | 6.8 | 2.9 | 2.3 | 2.3 | 2.2 | 0.2 | 1 | 1 | 2
|  | Plantation Road | 2.9 | 2.3 | 0.9 | 0.8 | 1.7 | 1.6 | 1.4 | 1.4 | 0.3
|  | South West Wanaka | 1 | 0.6 | 0.9 | 0.9 | 0.3 | 0.3 | 1 | 1 | 1.1
|  | Western & CBD | 2 | 15.4 | 0.3 | 5.8 | 12.5 | 11 | 16.4 | 11 | 13
| Wanaka Total |  | 36.1 | 28.8 | 9.1 | 14.9 | 23.4 | 16.1 | 24.69 | 19.9 | 21.8 | 3119.04 | 1138449.6 | 4290682 | Wanaka | 26.53% | 21.59%
Wanaka Total |  |  | 46.3 | 31.5 | 13.6 | 21.2 | 26.5 | 17 | 28.47 | 22.5 | 23.2 | 4000.32
Grand Total |  |  | 147.86 | 136.63 | 101.85 | 112.32 | 121.2 | 73.96 | 87.21 | 112.1 | 166.1 | 12775.104

## Leakage Guide
| THIS WORKSHEET PROVIDES AN OVERVIEW OF POSSIBLE OPPORTUNITIES AND ACTIONS FOR IMPROVING LEAKAGE MANAGEMENT PERFORMANCE | [10 empty] | ILI | BAND
| World Bank Institute (WBI) Guidelines | [9 empty] | B | 0 | A
| The World Bank Institute has recently introduced, into its NRW Training Modules, a target matrix for Real Losses management performance, based on real losses in volume/service connection/day for a range of average operating pressures, and classified into Bands A to D. The targets assume that customer meters are located at the property boundary, with an average connection density of around 40 per km mains. Bands A to D in the WBI target matrix can also be shown as an equivalent range of ILIs, which can be applied to a wider range of connection densities and customer meter locations, as shown below. Band limits in terms of ILIs, general descriptions of each Band, and appropriate recommended actions are as follows: | [10 empty] | 1 | A
| Developed Countries | BAND | Calculated ILI for this System | General description of Real Loss Management Performance Categories for Developed and Developing Countries | [7 empty] | 2 | B
[12 empty] | 3 | B
| ILI range | [10 empty] | 4 | C
1 | Less than 2 | A |  | Further loss reduction may be uneconomic unless there are shortages; careful analysis needed to identify cost-effective improvement | [7 empty] | 5 | C
3 | 2 to < 4 | B |  | Potential for marked improvements; consider pressure management, better active leakage control practices, and better network maintenance | [7 empty] | 6 | C
6 | 4 to < 8 | C |  | Poor leakage record; tolerable only if water is plentiful and cheap; even then, analyze level and nature of leakage and intensify leakage reduction efforts | [7 empty] | 7 | C
10 | 8 or more | D |  | Very inefficient use of resources; leakage reduction programs imperative and high priority | [7 empty] | 8 | D
[7 empty] | Priority Recommendations for WBI BANDS | A | B | C | D
|  | ILIs | Band A/B | Band B/C | Band C/D | This system
|  | 0.7 | 2 | 4 | 8 | 2.2501 | Investigate pressure management options * | Yes | Yes | Yes
|  | 1 | 2 | 4 | 8 | 2.2501
|  | 1 | 2 | 4 | 8 | 2.2501 | Investigate speed and quality of repairs | Yes | Yes | Yes
|  | 1 | 2 | 4 | 8 | 2.2501
|  | 1 | 2 | 4 | 8 | 2.2501 | Check economic intervention frequency ** | Yes | Yes
|  | 1.1 | 2 | 4 | 8 | 2.2501
|  | 1.2 | 2 | 4 | 8 | 2.2501 | Introduce/improve active leakage control ** | Yes | Yes | Yes
|  | 1.2 | 2 | 4 | 8 | 2.2501
|  | 1.2 | 2 | 4 | 8 | 2.2501 | Identify options for improved maintenance |  | Yes | Yes
|  | 1.35 | 2 | 4 | 8 | 2.2501
|  | 1.4 | 2 | 4 | 8 | 2.2501
|  | 1.5 | 2 | 4 | 8 | 2.2501 | Assess Economic Leakage Level | Yes | Yes
|  | 1.5 | 2 | 4 | 8 | 2.2501
|  | 1.6 | 2 | 4 | 8 | 2.2501
|  | 1.6 | 2 | 4 | 8 | 2.2501 | Review break frequencies |  | Yes | Yes
|  | 1.6 | 2 | 4 | 8 | 2.2501
|  | 1.7 | 2 | 4 | 8 | 2.2501
|  | 1.8 | 2 | 4 | 8 | 2.2501 | Review asset management policy |  | Yes | Yes | Yes
|  | 2.5 | 2 | 4 | 8 | 2.2501
|  | 3.6 | 2 | 4 | 8 | 2.2501
|  | 3.6 | 2 | 4 | 8 | 2.2501 | Deal with deficiencies in manpower, training and communications |  |  | Yes | Yes
|  | 5.8 | 2 | 4 | 8 | 2.2501
[7 empty] | 5-year plan to achieve next lowest band |  |  | Yes | Yes
[7 empty] | Fundamental peer review of all activities |  |  |  | Yes
Important Footnote: the Infrastructure Leakage Index (ILI) provides guidance as to how well real losses are being managed (in terms of repairs, active leakage control and infrastructure management) at the current operating pressure. However, calculation of the ILI does not imply that pressure management in a system is optimal, or economic. If system pressures are excessive, or subject to surges, then pressure management may result in additional benefits for real losses management - in particular, a reduction in new burst frequency and annual repair costs, and a reduction in flow rates of existing leaks. So even if a low ILI is being achieved, there may still be opportunities to reduce annual real losses by improved pressure management.
* The PMOpportunities Worksheet provides a quick overview of pressure management opportunities. See www.leakssuite.com for other pressure management software.
** Simplified methods of calculating an economic frequency of intervention for active leakage control by regular survey have been developed and are included in the LEAKSSuite ALCCalcs Standard software which also includes a terminology and basic analysis for components of night flows and performance indicators for night flows.
For a quick estimate of the probable benefits of Pressure Management for your system, go next to the 'PMOpportunities' Worksheet >>>>
Any other comments